## Exec. Works Cert, Form
APPENDIX I
LIST OF PROJECT PLANNED ACTIVITIES
PROJECT NAME: PREVENTIVE, PREDICTIVE AND CORRECTIVE MAINTENANCE OF 220/66/22KV AND LOW VOLTAGE ELECTRICAL BULK INFRASTRUCTURE OF BENGA MINE OPERATIONS 2021 -2022.
Two Years Schedule
Asset Description | Asset Type Description | Componets | Location | Tasks | Schedule | Total Project Quantity | Monthly Price [USD] | AnnualTotal Price [USD] | Certified Amount [USD] | Outstanding Amount [USD]
66 KV Lines | 66 KV Lines | Matambo-Benga Line | Matambo-Benga | → Visual Inspection | Quarterly | 8 | 860 | 6880
|  |  |  | →Verify Access Ways | Quarterly | 8 | 920 | 7360
|  |  |  | → Check and record ground resistance | Annual | 2 | 5600 | 11200
|  |  |  | →Thermal and Corona Inspection | Quarterly | 8 | 1500 | 12000
66 KV Lines | 66 KV Lines | Benga-Moatize | Moatize-Benga | → Visual Inspection | Quarterly | 8 | 660 | 5280
|  |  |  | →Verify Access Ways | Quarterly | 8 | 790 | 6320
|  |  |  | → Check and record ground resistance | Annual | 2 | 5600 | 11200
|  |  |  | →Thermal and Corona Inspection | Quarterly | 8 | 1100 | 8800
220 KV Bus Bar | 220 KV Bus Bar | Bus Bars | Matambo | →Re-Torque conexions | Annual | 2 | 270 | 540
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 66 | 132
66 KV Bus Bar | Main 66 KV Bus Bar | Bus Bars | Matambo | →Re-Torque conexions | Annual | 2 | 260 | 520
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 66 | 132
66 KV Bus Bar | Main 66 KV Bus Bar | Bus Bars | Benga | →Re-Torque conexions | Annual | 2 | 270 | 540
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 66 | 132
Transformer 66KV Outgoing Circuit | Transformer 66KV Bay | SF6 Circuit Breaker | Matambo | →Retightning connections | Annual | 2 | 10 | 20
|  |  |  | →Protection Test |  | 2 | 1200 | 2400
|  |  |  | →Selector Switch Test |  | 2 | 5 | 10
|  |  |  | →Check Signaling Lights |  | 2 | 5 | 10
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 66 | 132
|  |  |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300
|  | Isolator |  | →Lubricate |  | 2 | 15 | 30
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320
|  |  |  | →Re-Torque conexions | Annual | 2 | 15 | 30
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40
|  | Earth Switch |  | →Check Funtional test and auxilary contacts |  | 2 | 23 | 46
|  |  |  | →Check Signaling Light |  | 2 | 15 | 30
Transformer 66KV Incoming Circuit 1 | Transformer 66KV Bay | SF6 Circuit Breaker | Benga | →Retightning connections | Annual | 2 | 66 | 132
|  |  |  | →Protection Test |  | 2 | 1200 | 2400
|  |  |  | →Selector Switch Test |  | 2 | 5 | 10
|  |  |  | →Check Signaling Lights |  | 2 | 5 | 10
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 66 | 132
|  |  |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300
|  | Rotary Isolator |  | →Lubricate |  | 2 | 35 | 70
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320
|  |  |  | →Re-Torque conexions | Annual | 2 | 15 | 30
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40
|  | Earth Switch |  | →Check Funtional test and auxilary contacts |  | 2 | 23 | 46
|  |  |  | →Check Signaling Light |  | 2 | 15 | 30
Transformer 66KV Incoming Circuit 2 | Transformer 66KV Bay | SF6 Circuit Breaker | Benga | →Retightning connections | Annual | 2 | 66 | 132
|  |  |  | →Protection Test |  | 2 | 1200 | 2400
|  |  |  | →Selector Switch Test |  | 2 | 5 | 10
|  |  |  | →Check Signaling Lights |  | 2 | 5 | 10
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 150 | 300
|  |  |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300
|  | Rotary Isolator |  | →Lubricate |  | 2 | 35 | 70
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320
|  |  |  | →Re-Torque conexions | Annual | 2 | 15 | 30
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40
|  | Earth Switch |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300
|  |  |  | →Check Signaling Light |  | 2 | 5 | 10
Bus Coupler Panel 66KV | Bus Coupler Bay 66KV | SF6 Circuit Breaker | Matambo | →Retightning connections | Annual | 2 | 66 | 132
|  |  |  | →Protection Test |  | 2 | 1200 | 2400
|  |  |  | →Selector Switch Test |  | 2 | 5 | 10
|  |  |  | →Check Signaling Lights |  | 2 | 5 | 10
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40
|  |  |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300
|  | Isolator |  | →Lubricate |  | 2 | 35 | 70
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320
|  |  |  | →Re-Torque conexions | Annual | 2 | 15 | 30
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40
|  | Earth Switch |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300
|  |  |  | →Check Signaling Light |  | 2 | 5 | 10
Bus Coupler Panel 66KV | Bus Coupler Bay 66KV | Circuit Breaker | Benga | →Retightning connections | Annual | 2 | 66 | 132
|  |  |  | →Protection Test |  | 2 | 1200 | 2400
|  |  |  | →Selector Switch Test |  | 2 | 5 | 10
|  |  |  | →Check Signaling Lights |  | 2 | 5 | 10
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40
|  |  |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300
|  | Isolator |  | →Lubricate |  | 2 | 35 | 70
|  |  |  | →Check and record Temperature (Celcius) | Montly | 24 | 55 | 1320
|  |  |  | →Re-Torque conexions | Annual | 2 | 15 | 30
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40
|  | Earth Switch |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300
|  |  |  | →Check Signaling Light |  | 2 | 5 | 10
Benga Line 66KV | Benga Line Bay 66KV | SF6 Circuit Breaker | Matambo | →Retightning connections | Annual | 2 | 66 | 132
|  |  |  | →Protection Test |  | 2 | 1200 | 2400
|  |  |  | →Selector Switch Test |  | 2 | 5 | 10
|  |  |  | →Check Signaling Lights |  | 2 | 5 | 10
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40
|  |  |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300
|  | Isolator |  | →Lubricate |  | 2 | 35 | 70
|  |  |  | →Check and record Temperature (Celcius) | Montlhy | 24 | 55 | 1320
|  |  |  | →Re-Torque conexions | Annual | 2 | 15 | 30
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40
|  | Earth Switch |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300
|  |  |  | →Check Sinalization |  | 2 | 5 | 10
Benga Incomer Line 1 66KV | Benga Incomer Line 1 Bay 66KV | SF6 Circuit Breaker | Benga | →Retightning connections | Annual | 2 | 66 | 132
|  |  |  | →Protection Test |  | 2 | 1200 | 2400
|  |  |  | →Selector Switch Test |  | 2 | 5 | 10
|  |  |  | →Check Signaling Lights |  | 2 | 5 | 10
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40
|  |  |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300
|  | Isolator |  | →Lubricate |  | 2 | 35 | 70
|  |  |  | →Check and record Temperature (Celcius) | Montlhy | 24 | 55 | 1320
|  |  |  | →Re-Torque conexions | Annual | 2 | 15 | 30
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40
|  | Earth Switch |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300
|  |  |  | →Check Sinalization |  | 2 | 5 | 10
Transformer Incomer 2 66KV | Benga Incomer Line 2 Bay 66KV | SF6 Circuit Breaker | Benga | →Retightning connections | Annual | 2 | 66 | 132
|  |  |  | →Protection Test |  | 2 | 1200 | 2400
|  |  |  | →Selector Switch Test |  | 2 | 5 | 10
|  |  |  | →Check Signaling Lights |  | 2 | 5 | 10
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40
|  |  |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300
|  | Isolator |  | →Lubricate |  | 2 | 35 | 70
|  |  |  | →Check and record Temperature (Celcius) | Montlhy | 24 | 55 | 1320
|  |  |  | →Re-Torque conexions | Annual | 2 | 15 | 30
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40
|  | Earth Switch |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300
|  |  |  | →Check Sinalization |  | 2 | 5 | 10
Transformer Incomer 220KV | Benga Incomer Line 2 Bay 66KV | SF6 Circuit Breaker | Matambo | →Retightning connections | Annual | 2 | 66 | 132
|  |  |  | →Protection Test |  | 2 | 1200 | 2400
|  |  |  | →Selector Switch Test |  | 2 | 5 | 10
|  |  |  | →Check Signaling Lights |  | 2 | 5 | 10
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40
|  |  |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300
|  | Isolator |  | →Lubricate |  | 2 | 35 | 70
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320
|  |  |  | →Re-Torque conexions | Annual | 2 | 15 | 30
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40
|  | Earth Switch |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300
|  |  |  | →Check Sinalization |  | 2 | 5 | 10
Transformer Outgoing Circuit 22 KV | Transformer Outgoing Circuit Bay 22 KV | Rotary Isolator | Benga | →Lubricate | Annual | 2 | 35 | 70
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320
|  |  |  | →Re-Torque conexions | Annual | 2 | 15 | 30
|  |  |  | →Visual Inspection and Cleaning | Annual | 2 | 20 | 40
Transformer 1 - 20 MVA 66/22 KV | 20 MVA 66/22 KV Power Transformer | Transformer | Benga | →Check and record DC Winding Resistance | Annual | 2 | 1200 | 2400
|  |  |  | →Turns Ratio test | Annual | 2 | 1500 | 3000
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320
|  |  |  | →Instrumentation Test | Annual | 2 | 220 | 440
|  |  |  | → Check Leakage | Annual | 2 | 55 | 110
|  |  |  | →Re-Torque conexions | Annual | 2 | 280 | 560
|  | Insulation Oil |  | →Dissolved Gas Analysis (DGA) test | Biannual | 4 | 40 | 160
|  |  |  | →Dielectric Strength test |  | 4 | 40 | 160
|  |  |  | →Moisture test |  | 4 | 40 | 160
|  |  |  | →Power Factor/Dissipation Factor test |  | 4 | 40 | 160
|  |  |  | →Interfacial Tension test |  | 4 | 40 | 160
|  |  |  | →Acidity test |  | 4 | 40 | 160
|  |  |  | →Furans test |  | 4 | 40 | 160
|  |  |  | →Oxygen Inhibitor test |  | 4 | 40 | 160
|  | Cooling System |  | →Visual Inspection and Cleaning | Annual | 2 | 500 | 1000
Transformer 2 - 20 MVA 66/22 KV | 20 MVA 66/22 KV Power Transformer | Transformer | Benga | →Check and record DC Winding Resistance | Annual | 2 | 1200 | 2400
|  |  |  | →Turns Ratio test | Annual | 2 | 1500 | 3000
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320
|  |  |  | →Instrumentation Test | Annual | 2 | 220 | 440
|  |  |  | → Check Leakage | Annual | 2 | 55 | 110
|  |  |  | →Re-Torque conexions | Annual | 2 | 280 | 560
|  | Insulation Oil |  | →Dissolved Gas Analysis (DGA) test | Biannual | 4 | 40 | 160
|  |  |  | →Dielectric Strength test |  | 4 | 40 | 160
|  |  |  | →Moisture test |  | 4 | 40 | 160
|  |  |  | →Power Factor/Dissipation Factor test |  | 4 | 40 | 160
|  |  |  | →Interfacial Tension test |  | 4 | 40 | 160
|  |  |  | →Acidity test |  | 4 | 40 | 160
|  |  |  | →Furans test |  | 4 | 40 | 160
|  |  |  | →Oxygen Inhibitor test |  | 4 | 40 | 160
45 MVA 66/22 KV Power Transformer |  | Cooling System | Matambo | →Visual Inspection and Cleaning | Annual | 2 | 500 | 1000
| 45 MVA 66/22 KV Power Transformer | Transformer |  | →Check and record DC Winding Resistance | Annual | 2 | 1200 | 2400
|  |  |  | →Turns Ratio test | Annual | 2 | 1500 | 3000
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320
|  |  |  | →Instrumentation Test | Annual | 2 | 220 | 440
|  |  |  | →Check leakage | Annual | 2 | 55 | 110
|  |  |  | →Re-Torque conexions | Annual | 2 | 280 | 560
|  | Insulation Oil |  | →Dissolved Gas Analysis (DGA) test | Biannual | 4 | 40 | 160
|  |  |  | →Dielectric Strength test |  | 4 | 40 | 160
|  |  |  | →Moisture test |  | 4 | 40 | 160
|  |  |  | →Power Factor/Dissipation Factor test |  | 4 | 40 | 160
|  |  |  | →Interfacial Tension test |  | 4 | 40 | 160
|  |  |  | →Acidity test |  | 4 | 40 | 160
|  |  |  | →Furans test |  | 4 | 40 | 160
|  |  |  | →Oxygen Inhibitor test |  | 4 | 40 | 160
|  | Cooling System |  | →Check flow | Annual | 2 | 500 | 1000
|  |  |  | →Visual Inspection and Cleaning | Annual | 2 | 20 | 40
Auxiliary Transformer | 500KVA, 33/0.4KV, 50Hz, Auxiliary Transformer | Transformer | Matambo | →Re-Torque conexions | Annual | 2 | 15 | 30
|  |  |  | →Instrumentation Test | Annual | 2 | 24 | 48
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320
|  | Insulation Oil |  | →Dissolved Gas Analysis (DGA) test | Biannual | 4 | 40 | 160
|  |  |  | →Dielectric Strength test |  | 4 | 40 | 160
|  |  |  | →Moisture test |  | 4 | 40 | 160
|  |  |  | →Power Factor/Dissipation Factor test |  | 4 | 40 | 160
|  |  |  | →Interfacial Tension test |  | 4 | 40 | 160
|  |  |  | →Acidity test |  | 4 | 40 | 160
|  |  |  | →Furans test |  | 4 | 40 | 160
|  |  |  | →Oxygen Inhibitor test |  | 4 | 40 | 160
Auxiliary Transformer 1 | 100KVA, 22/0.4KV, 50Hz, Auxiliary Transformer | Transformer | Benga | →Re-Torque conexions | Annual | 2 | 15 | 30
|  |  |  | →Instrumentation Test | Annual | 2 | 24 | 48
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320
|  | Insulation Oil |  | →Dissolved Gas Analysis (DGA) test | Biannual | 4 | 40 | 160
|  |  |  | →Dielectric Strength test |  | 4 | 40 | 160
|  |  |  | →Moisture test |  | 4 | 40 | 160
|  |  |  | →Power Factor/Dissipation Factor test |  | 4 | 40 | 160
|  |  |  | →Interfacial Tension test |  | 4 | 40 | 160
|  |  |  | →Acidity test |  | 4 | 40 | 160
|  |  |  | →Furans test |  | 4 | 40 | 160
|  |  |  | →Oxygen Inhibitor test |  | 4 | 40 | 160
Auxiliary Transformer 2 | 100KVA, 22/0.4KV, 50Hz, Auxiliary Transformer | Transformer | Benga | →Re-Torque conexions | Annual | 2 | 15 | 30
|  |  |  | →Instrumentation Test | Annual | 2 | 24 | 48
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320
|  | Insulation Oil |  | →Dissolved Gas Analysis (DGA) test | Biannual | 4 | 40 | 160
|  |  |  | →Dielectric Strength test |  | 4 | 40 | 160
|  |  |  | →Moisture test |  | 4 | 40 | 160
|  |  |  | →Power Factor/Dissipation Factor test |  | 4 | 40 | 160
|  |  |  | →Interfacial Tension test |  | 4 | 40 | 160
|  |  |  | →Acidity test |  | 4 | 40 | 160
|  |  |  | →Furans test |  | 4 | 40 | 160
|  |  |  | →Oxygen Inhibitor test |  | 4 | 40 | 160
Auxiliary Services | Auxiliary Services | 400 V, 50Hz, 100KVA Main Board | Matambo | →Re-Torque conexions | Annual | 2 | 75 | 150
|  |  |  | → Protetion test |  | 2 | 180 | 360
|  |  |  | → Control Logical circuit Chec |  | 2 | 105 | 210
|  |  |  | → Cleaning |  | 2 | 32 | 64
|  | UPS |  | →Operation Check |  | 2 | 30 | 60
|  |  |  | →Cleaning |  | 2 | 15 | 30
|  |  |  | →Re-Torque conexions |  | 2 | 32 | 64
|  | Batteries |  | →Battery Solution Level Check |  | 2 | 17 | 34
|  |  |  | →Cleaning |  | 2 | 17 | 34
|  |  |  | →Battery Voltage Test |  | 2 | 380 | 760
|  |  |  | →Battery Load Test |  | 2 | 120 | 240
Auxiliary Services | Auxiliary Services | 400 V, 50Hz, 100KVA Main Board | Benga | →Re-Torque conexions | Annual | 2 | 180 | 360
|  |  |  | → Protetion test |  | 2 | 105 | 210
|  |  |  | → Control Logical circuit Chec |  | 2 | 32 | 64
|  |  |  | → House keeping |  | 2 | 30 | 60
|  | Battery Chager |  | →Operation Check |  | 2 | 15 | 30
|  |  |  | →Cleaning |  | 2 | 32 | 64
|  |  |  | →Re-Torque conexions |  | 2 | 17 | 34
|  | Batteries |  | →Battery Solution Level Check |  | 2 | 17 | 34
|  |  |  | →Cleaning |  | 2 | 380 | 760
|  |  |  | →Battery Voltage Test |  | 2 | 120 | 240
|  |  |  | →Battery Load Test |  | 2 |  | 0
Substation Yard | Substation Yard | Substation Yard | Matambo | → House keeping | Monthly | 24 | 400 | 9600
|  |  |  | → Outdoorung Lighting Inspection |  | 24 | 45 | 1080
Substation Yard | Substation Yard | Substation Yard | Benga | → House keeping | Monthly | 24 | 400 | 9600
|  |  |  | → Outdoorung Lighting Inspection |  | 24 | 45 | 1080
Control Room Building | Control Room Building | Control Room Building | Matambo | →House Keeping | Monthly | 24 | 400 | 9600
|  |  |  | → Indoor Lighting Inspection |  | 24 | 45 | 1080
Control Room Building | Control Room Building | Control Room Building | Benga | →House Keeping | Monthly | 24 | 400 | 9600
|  |  |  | → Indoor Lighting Inspection |  | 24 | 45 | 1080
66 KV Bushing | 66 KV Bushing | 66 KV Bushing | Matambo | →Capacitance test | Annual | 2 | 1500 | 3000
|  |  |  | →Dielectric Loss test |  | 2 | 1200 | 2400
|  |  |  | →Power Factor test |  | 2 | 1100 | 2200
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320
|  |  |  | →Visual Inspection and Cleaning | Annual | 2 | 33 | 66
66 KV Bushing | 66 KV Bushing | 66 KV Bushing | Benga | →Capacitance test | Annual | 2 | 1500 | 3000
|  |  |  | →Dielectric Loss test |  | 2 | 1200 | 2400
|  |  |  | →Power Factor test |  | 2 | 1100 | 2200
|  |  |  | →Check and record Temperature (Celcius) | Montlhy | 24 | 55 | 1320
|  |  |  | →Visual Inspection and Cleaning | Annual | 2 | 35 | 70
220 KV Bushings | 220 KV Bushing | 220 KV Bushing | Matambo | →Capacitance test | Annual | 2 | 1500 | 3000
|  |  |  | →Dielectric Loss test |  | 2 | 1200 | 2400
|  |  |  | →Power Factor test |  | 2 | 1100 | 2200
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320
|  |  |  | →Visual Inspection and Cleaning | Annual | 2 | 33 | 66
22 KV Bushing | 22KV Bushing | 22KV Bushing | Benga | →Capacitance test | Annual | 2 | 1500 | 3000
|  |  |  | →Dielectric Loss test |  | 2 | 1200 | 2400
|  |  |  | →Power Factor test |  | 2 | 1100 | 2200
|  |  |  | →Check and record Temperature (Celcius) | Montlhy | 24 | 55 | 1320
|  |  |  | →Visual Inspection and Cleaning | Annual | 2 | 33 | 66
Safty Signs | Safety Signs | Safety Signs | Matambo | →Check Saftey Signs | Annual | 2 | 20 | 40
|  |  |  | →Check Fire Extinguisher |  | 2 | 15 | 30
Safyt Signs | Safety Signs | Safety Signs | Benga | →Check Sfatey Signs | Annual | 2 | 20 | 40
|  |  |  | →Check Fire Extinguisher |  | 2 | 15 | 30
22 KV Consumer Susbation |  | 22 KV Switchgear and Auxiliares | Benga | →House keeping | Monthly | 24
|  |  |  | →Check Circuit Breaker Operational Function | Annual | 2
|  |  |  | →Check Functional of Sinalization | Annual | 2
|  |  |  | →Panel and Circuit Breaker visual Inspection and Cleaning | Annual | 2
|  |  |  | →Check heater resistance | Biannual | 4
|  |  |  | →Cable 22KV Terminal Inspection | Biannual | 4
|  |  |  | →Cable 22KV Insulation Test | Biannual | 4
|  |  |  | →Protection test and report | Annual | 2
|  |  |  | →Circuit Breaker Timing and Contact Resistance test | Annual | 2
Lines 22KV |  | Lines 22 KV | Benga | →Check Access | Monthly | 24
|  |  |  | →Wood poles inspection | Monthly | 24
|  |  |  | →Insulator Inspection and connections | Quarterly | 8
|  |  |  | →Termites control | Annual | 2
|  |  |  | →Inspect the lines tension | Monthly | 24
|  |  |  | →Inspect Line structure integrity | Monthly | 24
MCC's RMU 22KV |  | MCC's RMU 22KV | Benga | →Visual Inspection | Quarterly | 8
|  |  |  | →Cleaning | Quarterly | 8
|  |  |  | →Protection test and report | Annual | 2
|  |  |  | →Check Fuctional buttom test and sinalization | Annual | 2
|  |  |  | →Insulation Test | Annual | 2
Mini Subastion 22KV/33KV up to 2500 KVA |  | Transformers up to 2500 KVA (18 small transformer) | Benga | →Re-Torque conexions | Annual | 2
|  |  |  | →Instrumentation Test | Annual | 2
|  |  |  | →Cable termination inspection | Biannual | 4
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24
|  | Transformer Oil (18 smallTransformers) |  | →Dissolved Gas Analysis (DGA) test | Biannual | 4
|  |  |  | →Dielectric Strength test | Biannual | 4
|  |  |  | →Moisture test | Biannual | 4
|  |  |  | →Power Factor/Dissipation Factor test | Biannual | 4
|  |  |  | →Interfacial Tension test | Biannual | 4
|  |  |  | →Acidity test | Biannual | 4
|  |  |  | →Furans test | Biannual | 4
|  |  |  | →Oxygen Inhibitor test | Biannual | 4
|  | Transformer Panel Low voltage (18 small transformer) |  | →Re-Torque conexions | Annual | 2
|  |  |  | → Protetion test | Annual | 2
|  |  |  | → Control Logical circuit Chec | Annual | 2
|  |  |  | → Cleaning | Quarterly | 8
Outdoor Lighiting |  | Outdoor Lighting | CHPP, Rail Siding, Training Centre, Camp Site, Core yard, 400 Man Camp, Main Gate to the Mine, Exploration Camp | → Check Light Structural Integrity, check light circuit functional, qood pole inspection, termites control and report | Monthly | 24

## Breakdown Call Out Rates (hidden)
BREAKDOWN CALL OUT RATES RATES FOR 220kV/66KV INFRASTRUCTURE MAINTENANCE SERVICES (including 66kV OHL, 220/66kV Apparatus and Equipments at Matambo Su and Benga Sub)
STAFF RATES PER HOUR | Fault Finding Rate [USD]
| Engineer | Senior Technician | Technician | Assistant
Week days & Saturday 100% | 55 | 37 | 22 | 15
Sundays & Pubblic Hollidays 200% | 110 | 74 | 44 | 30
SPECIAL MACHINARY AND EQUIPMENT | Mobilization [USD] | Demobilization [USD] | Equipment Rate/Hour [USD] | Operator Rate-Hour [USD]
Dozer | 2000 | 2000 | 250 | 13
Excavator | 1100 | 1100 | 120 | 13
Cherry Pick | 325 | 325 | 95 | 10
Boat Rental | ­ | ­ | 85 | ­
Transformer Oil Plant | 900 | 900 | 80 | 45