## Exec. Works Cert, Form
ANNEX F
BILL OF QUANTITIES - BoQ
PROJECT NAME: PREVENTIVE, PREDICTIVE AND CORRECTIVE MAINTENANCE OF 220/66/22KV AND LOW VOLTAGE ELECTRICAL BULK INFRASTRUCTURE OF BENGA MINE OPERATIONS 2021 -2022.
Shedule for Two Years
Asset Description | Asset Type Description | Componets | Location | Tasks | Unit | Total Project Quantity | Monthly Price [USD] | AnnualTotal Price [USD] | Unit Price [USD] | Project Total Price [USD] | Certified Amount [USD] | Outstanding Amount [USD]
66 KV Lines | 66 KV Lines | Matambo-Benga Line | Matambo-Benga | → Visual Inspection | Quarterly | 8 | 860 | 6880 |  | 0
|  |  |  | →Verify Access Ways | Quarterly | 8 | 920 | 7360 |  | 0
|  |  |  | → Check and record ground resistance | Annual | 2 | 5600 | 11200 |  | 0
|  |  |  | →Thermal and Corona Inspection | Quarterly | 8 | 1500 | 12000 |  | 0
66 KV Lines | 66 KV Lines | Benga-Moatize | Moatize-Benga | → Visual Inspection | Quarterly | 8 | 660 | 5280 |  | 0
|  |  |  | →Verify Access Ways | Quarterly | 8 | 790 | 6320 |  | 0
|  |  |  | → Check and record ground resistance | Annual | 2 | 5600 | 11200 |  | 0
|  |  |  | →Thermal and Corona Inspection | Quarterly | 8 | 1100 | 8800 |  | 0
220 KV Bus Bar | 220 KV Bus Bar | Bus Bars | Matambo | →Re-Torque conexions | Annual | 2 | 270 | 540 |  | 0
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 66 | 132 |  | 0
66 KV Bus Bar | Main 66 KV Bus Bar | Bus Bars | Matambo | →Re-Torque conexions | Annual | 2 | 260 | 520 |  | 0
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 66 | 132 |  | 0
66 KV Bus Bar | Main 66 KV Bus Bar | Bus Bars | Benga | →Re-Torque conexions | Annual | 2 | 270 | 540 |  | 0
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 66 | 132 |  | 0
Transformer 66KV Outgoing Circuit | Transformer 66KV Bay | SF6 Circuit Breaker | Matambo | →Retightning connections | Annual | 2 | 10 | 20 |  | 0
|  |  |  | →Protection Test |  | 2 | 1200 | 2400 |  | 0
|  |  |  | →Selector Switch Test |  | 2 | 5 | 10 |  | 0
|  |  |  | →Check Signaling Lights |  | 2 | 5 | 10 |  | 0
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 66 | 132 |  | 0
|  |  |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300 |  | 0
|  | Isolator |  | →Lubricate |  | 2 | 15 | 30 |  | 0
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320 |  | 0
|  |  |  | →Re-Torque conexions | Annual | 2 | 15 | 30 |  | 0
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40 |  | 0
|  | Earth Switch |  | →Check Funtional test and auxilary contacts |  | 2 | 23 | 46 |  | 0
|  |  |  | →Check Signaling Light |  | 2 | 15 | 30 |  | 0
Transformer 66KV Incoming Circuit 1 | Transformer 66KV Bay | SF6 Circuit Breaker | Benga | →Retightning connections | Annual | 2 | 66 | 132 |  | 0
|  |  |  | →Protection Test |  | 2 | 1200 | 2400 |  | 0
|  |  |  | →Selector Switch Test |  | 2 | 5 | 10 |  | 0
|  |  |  | →Check Signaling Lights |  | 2 | 5 | 10 |  | 0
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 66 | 132 |  | 0
|  |  |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300 |  | 0
|  | Rotary Isolator |  | →Lubricate |  | 2 | 35 | 70 |  | 0
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320 |  | 0
|  |  |  | →Re-Torque conexions | Annual | 2 | 15 | 30 |  | 0
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40 |  | 0
|  | Earth Switch |  | →Check Funtional test and auxilary contacts |  | 2 | 23 | 46 |  | 0
|  |  |  | →Check Signaling Light |  | 2 | 15 | 30 |  | 0
Transformer 66KV Incoming Circuit 2 | Transformer 66KV Bay | SF6 Circuit Breaker | Benga | →Retightning connections | Annual | 2 | 66 | 132 |  | 0
|  |  |  | →Protection Test |  | 2 | 1200 | 2400 |  | 0
|  |  |  | →Selector Switch Test |  | 2 | 5 | 10 |  | 0
|  |  |  | →Check Signaling Lights |  | 2 | 5 | 10 |  | 0
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 150 | 300 |  | 0
|  |  |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300 |  | 0
|  | Rotary Isolator |  | →Lubricate |  | 2 | 35 | 70 |  | 0
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320 |  | 0
|  |  |  | →Re-Torque conexions | Annual | 2 | 15 | 30 |  | 0
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40 |  | 0
|  | Earth Switch |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300 |  | 0
|  |  |  | →Check Signaling Light |  | 2 | 5 | 10 |  | 0
Bus Coupler Panel 66KV | Bus Coupler Bay 66KV | SF6 Circuit Breaker | Matambo | →Retightning connections | Annual | 2 | 66 | 132 |  | 0
|  |  |  | →Protection Test |  | 2 | 1200 | 2400 |  | 0
|  |  |  | →Selector Switch Test |  | 2 | 5 | 10 |  | 0
|  |  |  | →Check Signaling Lights |  | 2 | 5 | 10 |  | 0
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40 |  | 0
|  |  |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300 |  | 0
|  | Isolator |  | →Lubricate |  | 2 | 35 | 70 |  | 0
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320 |  | 0
|  |  |  | →Re-Torque conexions | Annual | 2 | 15 | 30 |  | 0
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40 |  | 0
|  | Earth Switch |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300 |  | 0
|  |  |  | →Check Signaling Light |  | 2 | 5 | 10 |  | 0
Bus Coupler Panel 66KV | Bus Coupler Bay 66KV | Circuit Breaker | Benga | →Retightning connections | Annual | 2 | 66 | 132 |  | 0
|  |  |  | →Protection Test |  | 2 | 1200 | 2400 |  | 0
|  |  |  | →Selector Switch Test |  | 2 | 5 | 10 |  | 0
|  |  |  | →Check Signaling Lights |  | 2 | 5 | 10 |  | 0
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40 |  | 0
|  |  |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300 |  | 0
|  | Isolator |  | →Lubricate |  | 2 | 35 | 70 |  | 0
|  |  |  | →Check and record Temperature (Celcius) | Montly | 24 | 55 | 1320 |  | 0
|  |  |  | →Re-Torque conexions | Annual | 2 | 15 | 30 |  | 0
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40 |  | 0
|  | Earth Switch |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300 |  | 0
|  |  |  | →Check Signaling Light |  | 2 | 5 | 10 |  | 0
Benga Line 66KV | Benga Line Bay 66KV | SF6 Circuit Breaker | Matambo | →Retightning connections | Annual | 2 | 66 | 132 |  | 0
|  |  |  | →Protection Test |  | 2 | 1200 | 2400 |  | 0
|  |  |  | →Selector Switch Test |  | 2 | 5 | 10 |  | 0
|  |  |  | →Check Signaling Lights |  | 2 | 5 | 10 |  | 0
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40 |  | 0
|  |  |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300 |  | 0
|  | Isolator |  | →Lubricate |  | 2 | 35 | 70 |  | 0
|  |  |  | →Check and record Temperature (Celcius) | Montlhy | 24 | 55 | 1320 |  | 0
|  |  |  | →Re-Torque conexions | Annual | 2 | 15 | 30 |  | 0
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40 |  | 0
|  | Earth Switch |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300 |  | 0
|  |  |  | →Check Sinalization |  | 2 | 5 | 10 |  | 0
Benga Incomer Line 1 66KV | Benga Incomer Line 1 Bay 66KV | SF6 Circuit Breaker | Benga | →Retightning connections | Annual | 2 | 66 | 132 |  | 0
|  |  |  | →Protection Test |  | 2 | 1200 | 2400 |  | 0
|  |  |  | →Selector Switch Test |  | 2 | 5 | 10 |  | 0
|  |  |  | →Check Signaling Lights |  | 2 | 5 | 10 |  | 0
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40 |  | 0
|  |  |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300 |  | 0
|  | Isolator |  | →Lubricate |  | 2 | 35 | 70 |  | 0
|  |  |  | →Check and record Temperature (Celcius) | Montlhy | 24 | 55 | 1320 |  | 0
|  |  |  | →Re-Torque conexions | Annual | 2 | 15 | 30 |  | 0
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40 |  | 0
|  | Earth Switch |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300 |  | 0
|  |  |  | →Check Sinalization |  | 2 | 5 | 10 |  | 0
Transformer Incomer 2 66KV | Benga Incomer Line 2 Bay 66KV | SF6 Circuit Breaker | Benga | →Retightning connections | Annual | 2 | 66 | 132 |  | 0
|  |  |  | →Protection Test |  | 2 | 1200 | 2400 |  | 0
|  |  |  | →Selector Switch Test |  | 2 | 5 | 10 |  | 0
|  |  |  | →Check Signaling Lights |  | 2 | 5 | 10 |  | 0
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40 |  | 0
|  |  |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300 |  | 0
|  | Isolator |  | →Lubricate |  | 2 | 35 | 70 |  | 0
|  |  |  | →Check and record Temperature (Celcius) | Montlhy | 24 | 55 | 1320 |  | 0
|  |  |  | →Re-Torque conexions | Annual | 2 | 15 | 30 |  | 0
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40 |  | 0
|  | Earth Switch |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300 |  | 0
|  |  |  | →Check Sinalization |  | 2 | 5 | 10 |  | 0
Transformer Incomer 220KV | Benga Incomer Line 2 Bay 66KV | SF6 Circuit Breaker | Matambo | →Retightning connections | Annual | 2 | 66 | 132 |  | 0
|  |  |  | →Protection Test |  | 2 | 1200 | 2400 |  | 0
|  |  |  | →Selector Switch Test |  | 2 | 5 | 10 |  | 0
|  |  |  | →Check Signaling Lights |  | 2 | 5 | 10 |  | 0
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40 |  | 0
|  |  |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300 |  | 0
|  | Isolator |  | →Lubricate |  | 2 | 35 | 70 |  | 0
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320 |  | 0
|  |  |  | →Re-Torque conexions | Annual | 2 | 15 | 30 |  | 0
|  |  |  | →Visual Inspection and Cleaning |  | 2 | 20 | 40 |  | 0
|  | Earth Switch |  | →Check Funtional test and auxilary contacts |  | 2 | 150 | 300 |  | 0
|  |  |  | →Check Sinalization |  | 2 | 5 | 10 |  | 0
Transformer Outgoing Circuit 22 KV | Transformer Outgoing Circuit Bay 22 KV | Rotary Isolator | Benga | →Lubricate | Annual | 2 | 35 | 70 |  | 0
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320 |  | 0
|  |  |  | →Re-Torque conexions | Annual | 2 | 15 | 30 |  | 0
|  |  |  | →Visual Inspection and Cleaning | Annual | 2 | 20 | 40 |  | 0
Transformer 1 - 20 MVA 66/22 KV | 20 MVA 66/22 KV Power Transformer | Transformer | Benga | →Check and record DC Winding Resistance | Annual | 2 | 1200 | 2400 |  | 0
|  |  |  | →Turns Ratio test | Annual | 2 | 1500 | 3000 |  | 0
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320 |  | 0
|  |  |  | →Instrumentation Test | Annual | 2 | 220 | 440 |  | 0
|  |  |  | → Check Leakage | Annual | 2 | 55 | 110 |  | 0
|  |  |  | →Re-Torque conexions | Annual | 2 | 280 | 560 |  | 0
|  | Insulation Oil |  | →Dissolved Gas Analysis (DGA) test | Biannual | 4 | 40 | 160 |  | 0
|  |  |  | →Dielectric Strength test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Moisture test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Power Factor/Dissipation Factor test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Interfacial Tension test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Acidity test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Furans test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Oxygen Inhibitor test |  | 4 | 40 | 160 |  | 0
|  | Cooling System |  | →Visual Inspection and Cleaning | Annual | 2 | 500 | 1000 |  | 0
Transformer 2 - 20 MVA 66/22 KV | 20 MVA 66/22 KV Power Transformer | Transformer | Benga | →Check and record DC Winding Resistance | Annual | 2 | 1200 | 2400 |  | 0
|  |  |  | →Turns Ratio test | Annual | 2 | 1500 | 3000 |  | 0
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320 |  | 0
|  |  |  | →Instrumentation Test | Annual | 2 | 220 | 440 |  | 0
|  |  |  | → Check Leakage | Annual | 2 | 55 | 110 |  | 0
|  |  |  | →Re-Torque conexions | Annual | 2 | 280 | 560 |  | 0
|  | Insulation Oil |  | →Dissolved Gas Analysis (DGA) test | Biannual | 4 | 40 | 160 |  | 0
|  |  |  | →Dielectric Strength test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Moisture test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Power Factor/Dissipation Factor test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Interfacial Tension test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Acidity test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Furans test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Oxygen Inhibitor test |  | 4 | 40 | 160 |  | 0
45 MVA 66/22 KV Power Transformer |  | Cooling System | Matambo | →Visual Inspection and Cleaning | Annual | 2 | 500 | 1000 |  | 0
| 45 MVA 66/22 KV Power Transformer | Transformer |  | →Check and record DC Winding Resistance | Annual | 2 | 1200 | 2400 |  | 0
|  |  |  | →Turns Ratio test | Annual | 2 | 1500 | 3000 |  | 0
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320 |  | 0
|  |  |  | →Instrumentation Test | Annual | 2 | 220 | 440 |  | 0
|  |  |  | →Check leakage | Annual | 2 | 55 | 110 |  | 0
|  |  |  | →Re-Torque conexions | Annual | 2 | 280 | 560 |  | 0
|  | Insulation Oil |  | →Dissolved Gas Analysis (DGA) test | Biannual | 4 | 40 | 160 |  | 0
|  |  |  | →Dielectric Strength test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Moisture test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Power Factor/Dissipation Factor test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Interfacial Tension test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Acidity test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Furans test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Oxygen Inhibitor test |  | 4 | 40 | 160 |  | 0
|  | Cooling System |  | →Check flow | Annual | 2 | 500 | 1000 |  | 0
|  |  |  | →Visual Inspection and Cleaning | Annual | 2 | 20 | 40 |  | 0
Auxiliary Transformer | 500KVA, 33/0.4KV, 50Hz, Auxiliary Transformer | Transformer | Matambo | →Re-Torque conexions | Annual | 2 | 15 | 30 |  | 0
|  |  |  | →Instrumentation Test | Annual | 2 | 24 | 48 |  | 0
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320 |  | 0
|  | Insulation Oil |  | →Dissolved Gas Analysis (DGA) test | Biannual | 4 | 40 | 160 |  | 0
|  |  |  | →Dielectric Strength test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Moisture test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Power Factor/Dissipation Factor test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Interfacial Tension test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Acidity test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Furans test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Oxygen Inhibitor test |  | 4 | 40 | 160 |  | 0
Auxiliary Transformer 1 | 100KVA, 22/0.4KV, 50Hz, Auxiliary Transformer | Transformer | Benga | →Re-Torque conexions | Annual | 2 | 15 | 30 |  | 0
|  |  |  | →Instrumentation Test | Annual | 2 | 24 | 48 |  | 0
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320 |  | 0
|  | Insulation Oil |  | →Dissolved Gas Analysis (DGA) test | Biannual | 4 | 40 | 160 |  | 0
|  |  |  | →Dielectric Strength test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Moisture test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Power Factor/Dissipation Factor test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Interfacial Tension test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Acidity test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Furans test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Oxygen Inhibitor test |  | 4 | 40 | 160 |  | 0
Auxiliary Transformer 2 | 100KVA, 22/0.4KV, 50Hz, Auxiliary Transformer | Transformer | Benga | →Re-Torque conexions | Annual | 2 | 15 | 30 |  | 0
|  |  |  | →Instrumentation Test | Annual | 2 | 24 | 48 |  | 0
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320 |  | 0
|  | Insulation Oil |  | →Dissolved Gas Analysis (DGA) test | Biannual | 4 | 40 | 160 |  | 0
|  |  |  | →Dielectric Strength test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Moisture test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Power Factor/Dissipation Factor test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Interfacial Tension test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Acidity test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Furans test |  | 4 | 40 | 160 |  | 0
|  |  |  | →Oxygen Inhibitor test |  | 4 | 40 | 160 |  | 0
Auxiliary Services | Auxiliary Services | 400 V, 50Hz, 100KVA Main Board | Matambo | →Re-Torque conexions | Annual | 2 | 75 | 150 |  | 0
|  |  |  | → Protetion test |  | 2 | 180 | 360 |  | 0
|  |  |  | → Control Logical circuit Chec |  | 2 | 105 | 210 |  | 0
|  |  |  | → Cleaning |  | 2 | 32 | 64 |  | 0
|  | UPS |  | →Operation Check |  | 2 | 30 | 60 |  | 0
|  |  |  | →Cleaning |  | 2 | 15 | 30 |  | 0
|  |  |  | →Re-Torque conexions |  | 2 | 32 | 64 |  | 0
|  | Batteries |  | →Battery Solution Level Check |  | 2 | 17 | 34 |  | 0
|  |  |  | →Cleaning |  | 2 | 17 | 34 |  | 0
|  |  |  | →Battery Voltage Test |  | 2 | 380 | 760 |  | 0
|  |  |  | →Battery Load Test |  | 2 | 120 | 240 |  | 0
Auxiliary Services | Auxiliary Services | 400 V, 50Hz, 100KVA Main Board | Benga | →Re-Torque conexions | Annual | 2 | 180 | 360 |  | 0
|  |  |  | → Protetion test |  | 2 | 105 | 210 |  | 0
|  |  |  | → Control Logical circuit Chec |  | 2 | 32 | 64 |  | 0
|  |  |  | → House keeping |  | 2 | 30 | 60 |  | 0
|  | Battery Chager |  | →Operation Check |  | 2 | 15 | 30 |  | 0
|  |  |  | →Cleaning |  | 2 | 32 | 64 |  | 0
|  |  |  | →Re-Torque conexions |  | 2 | 17 | 34 |  | 0
|  | Batteries |  | →Battery Solution Level Check |  | 2 | 17 | 34 |  | 0
|  |  |  | →Cleaning |  | 2 | 380 | 760 |  | 0
|  |  |  | →Battery Voltage Test |  | 2 | 120 | 240 |  | 0
|  |  |  | →Battery Load Test |  | 2 |  | 0 |  | 0
Substation Yard | Substation Yard | Substation Yard | Matambo | → House keeping | Monthly | 24 | 400 | 9600 |  | 0
|  |  |  | → Outdoorung Lighting Inspection |  | 24 | 45 | 1080 |  | 0
Substation Yard | Substation Yard | Substation Yard | Benga | → House keeping | Monthly | 24 | 400 | 9600 |  | 0
|  |  |  | → Outdoorung Lighting Inspection |  | 24 | 45 | 1080 |  | 0
Control Room Building | Control Room Building | Control Room Building | Matambo | →House Keeping | Monthly | 24 | 400 | 9600 |  | 0
|  |  |  | → Indoor Lighting Inspection |  | 24 | 45 | 1080 |  | 0
Control Room Building | Control Room Building | Control Room Building | Benga | →House Keeping | Monthly | 24 | 400 | 9600 |  | 0
|  |  |  | → Indoor Lighting Inspection |  | 24 | 45 | 1080 |  | 0
66 KV Bushing | 66 KV Bushing | 66 KV Bushing | Matambo | →Capacitance test | Annual | 2 | 1500 | 3000 |  | 0
|  |  |  | →Dielectric Loss test |  | 2 | 1200 | 2400 |  | 0
|  |  |  | →Power Factor test |  | 2 | 1100 | 2200 |  | 0
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320 |  | 0
|  |  |  | →Visual Inspection and Cleaning | Annual | 2 | 33 | 66 |  | 0
66 KV Bushing | 66 KV Bushing | 66 KV Bushing | Benga | →Capacitance test | Annual | 2 | 1500 | 3000 |  | 0
|  |  |  | →Dielectric Loss test |  | 2 | 1200 | 2400 |  | 0
|  |  |  | →Power Factor test |  | 2 | 1100 | 2200 |  | 0
|  |  |  | →Check and record Temperature (Celcius) | Montlhy | 24 | 55 | 1320 |  | 0
|  |  |  | →Visual Inspection and Cleaning | Annual | 2 | 35 | 70 |  | 0
220 KV Bushings | 220 KV Bushing | 220 KV Bushing | Matambo | →Capacitance test | Annual | 2 | 1500 | 3000 |  | 0
|  |  |  | →Dielectric Loss test |  | 2 | 1200 | 2400 |  | 0
|  |  |  | →Power Factor test |  | 2 | 1100 | 2200 |  | 0
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 | 55 | 1320 |  | 0
|  |  |  | →Visual Inspection and Cleaning | Annual | 2 | 33 | 66 |  | 0
22 KV Bushing | 22KV Bushing | 22KV Bushing | Benga | →Capacitance test | Annual | 2 | 1500 | 3000 |  | 0
|  |  |  | →Dielectric Loss test |  | 2 | 1200 | 2400 |  | 0
|  |  |  | →Power Factor test |  | 2 | 1100 | 2200 |  | 0
|  |  |  | →Check and record Temperature (Celcius) | Montlhy | 24 | 55 | 1320 |  | 0
|  |  |  | →Visual Inspection and Cleaning | Annual | 2 | 33 | 66 |  | 0
Safty Signs | Safety Signs | Safety Signs | Matambo | Check Saftey Signs | Annual | 2 | 20 | 40 |  | 0
|  |  |  | Check Fire Extinguisher |  | 2 | 15 | 30 |  | 0
Safyt Signs | Safety Signs | Safety Signs | Benga | Check Sfatey Signs | Annual | 2 | 20 | 40 |  | 0
|  |  |  | Check Fire Extinguisher |  | 2 | 15 | 30 |  | 0
22 KV Consumer Susbation |  | 22 KV Switchgear and Auxiliares | Benga | House keeping | Monthly | 24 |  |  |  | 0
|  |  |  | Check Circuit Breaker Operational Function | Annual | 2 |  |  |  | 0
|  |  |  | Check Functional of Sinalization | Annual | 2 |  |  |  | 0
|  |  |  | Panel and Circuit Breaker visual Inspection and Cleaning | Annual | 2 |  |  |  | 0
|  |  |  | Check heater resistance | Quarterly | 8 |  |  |  | 0
|  |  |  | Cable 22KV Terminal Inspection | Quarterly | 8 |  |  |  | 0
|  |  |  | Cable 22KV Insulation Test | Quarterly | 8 |  |  |  | 0
|  |  |  | Protection test and report | Annual | 2 |  |  |  | 0
|  |  |  | Circuit Breaker Timing and Contact Resistance test | Annual | 2 |  |  |  | 0
Lines 22KV |  | Lines 22 KV | Benga | Check Access | Monthly | 24 |  |  |  | 0
|  |  |  | Wood poles inspection | Monthly | 24 |  |  |  | 0
|  |  |  | Insulator Inspection and connections | Quarterly | 8 |  |  |  | 0
|  |  |  | Termites control | Annual | 2 |  |  |  | 0
|  |  |  | Inspect the lines tension | Monthly | 24 |  |  |  | 0
|  |  |  | Inspect Line structure integrity | Monthly | 24 |  |  |  | 0
MCC's RMU 22KV |  | MCC's RMU 22KV | Benga | Visual Inspection | Quarterly | 8 |  |  |  | 0
|  |  |  | Cleaning | Quarterly | 8 |  |  |  | 0
|  |  |  | Protection test and report | Annual | 2 |  |  |  | 0
|  |  |  | Check Fuctional buttom test and sinalization | Annual | 2 |  |  |  | 0
|  |  |  | Insulation Test | Annual | 2 |  |  |  | 0
Mini Subastion 22KV/33KV up to 2500 KVA |  | Transformers up to 2500 KVA (18 small transformer) | Benga | →Re-Torque conexions | Annual | 2 |  |  |  | 0
|  |  |  | →Instrumentation Test | Annual | 2 |  |  |  | 0
|  |  |  | →Cable termination inspection | Biannual | 4 |  |  |  | 0
|  |  |  | →Check and record Temperature (Celcius) | Monthly | 24 |  |  |  | 0
|  | Transformer Oil (18 smallTransformers) |  | →Dissolved Gas Analysis (DGA) test | Biannual | 4 |  |  |  | 0
|  |  |  | →Dielectric Strength test | Biannual | 4 |  |  |  | 0
|  |  |  | →Moisture test | Biannual | 4 |  |  |  | 0
|  |  |  | →Power Factor/Dissipation Factor test | Biannual | 4 |  |  |  | 0
|  |  |  | →Interfacial Tension test | Biannual | 4 |  |  |  | 0
|  |  |  | →Acidity test | Biannual | 4 |  |  |  | 0
|  |  |  | →Furans test | Biannual | 4 |  |  |  | 0
|  |  |  | →Oxygen Inhibitor test | Biannual | 4 |  |  |  | 0
|  | Transformer Panel Low voltage (18 small transformer) |  | →Re-Torque conexions | Annual | 2 |  |  |  | 0
|  |  |  | → Protetion test | Annual | 2 |  |  |  | 0
|  |  |  | → Control Logical circuit Chec | Annual | 2 |  |  |  | 0
|  |  |  | → Cleaning | Quarterly | 8 |  |  |  | 0
Outdoor Lighiting |  | Outdoor Lighting | CHPP, Rail Siding, Training Centre, Camp Site, Core yard, 400 Man Camp, Main Gate to the Mine, Exploration Camp | → Check Light Structural Integrity, check light circuit functional, qood pole inspection, termites control and report | Monthly | 24 |  |  |  | 0
Project Human Resource |  | Engineer (1) | Benga | → Normal Hours | Hours | 2112 |  |  |  | 0
|  | Skilled electrician (2) |  |  | Hours | 4224 |  |  |  | 0
|  | Semi-skilled electrician (2) |  |  | Hours | 4224 |  |  |  | 0
|  | Lines man specialist (2) |  |  | Hours | 4224 |  |  |  | 0
|  | Safety Officer (1) |  |  | Hours | 4224 |  |  |  | 0
|  | Engineer (1) | Benga | → Extra Hours 50% | Hours | 422 |  |  |  | 0
|  | Skilled electrician (2) |  |  | Hours | 422 |  |  |  | 0
|  | Semi-skilled electrician (2) |  |  | Hours | 422 |  |  |  | 0
|  | Lines man specialist (2) |  |  | Hours | 422 |  |  |  | 0
|  | Safety Officer (1) |  |  | Hours | 422 |  |  |  | 0
|  | Engineer (1) | Benga | → Extra Hours 100% | Hours | 210 |  |  |  | 0
|  | Skilled electrician (2) |  |  | Hours | 210 |  |  |  | 0
|  | Semi-skilled electrician (2) |  |  | Hours | 210 |  |  |  | 0
|  | Lines man specialist (2) |  |  | Hours | 210 |  |  |  | 0
|  | Safety Officer (1) |  |  | Hours | 210 |  |  |  | 0
Equipments |  | Bulldozer D7 | Benga | → Bulldozer D7 | Hours | 400 |  |  |  | 0
|  | Craned truck 14Ton |  | → Craned truck 14Ton | Hours | 1200 |  |  |  | 0
|  | TLB 67KW |  | → TLB 67KW | Hours | 800 |  |  |  | 0
|  | Transformer Oil Purification Plant |  | → Transformer Oil Purification Plant | Hours | 432 |  |  |  | 0
|  | Boat rental |  | → Boat rental | Hours | 192 |  |  |  | 0
|  | Cherry Picker 230Kg |  | → Cherry Picker 230Kg | Hours | 1200 |  |  |  | 0
Mobilization & Demobilization |  | Mobilization | Benga | → Mobilization | GA | 1 |  |  |  | 0
|  | Demobilization |  | → Demobilization | GA | 1 |  |  |  | 0
Insurances |  | Insurances | Benga | → Insurances | GA | 1 |  |  |  | 0
Overheads |  | Overheads | Benga | → Overheads | GA | 1 |  |  |  | 0
Monthly Time Related Cost |  | Time Related Cost | Benga | → Time Related Cost | Monthly | 24 |  |  |  | 0
Montlhy Fixed Cost | → CleaningManagment Costs | Fixed Cost | Benga | → Fixed Cost | Monthly | 24 | 11800 | 283200 |  | 0
Total | [9 empty] | 0

## Breakdown Call Out Rates (hidden)
BREAKDOWN CALL OUT RATES RATES FOR 220kV/66KV INFRASTRUCTURE MAINTENANCE SERVICES (including 66kV OHL, 220/66kV Apparatus and Equipments at Matambo Su and Benga Sub)
STAFF RATES PER HOUR | Fault Finding Rate [USD]
| Engineer | Senior Technician | Technician | Assistant
Week days & Saturday 100% | 55 | 37 | 22 | 15
Sundays & Pubblic Hollidays 200% | 110 | 74 | 44 | 30
SPECIAL MACHINARY AND EQUIPMENT | Mobilization [USD] | Demobilization [USD] | Equipment Rate/Hour [USD] | Operator Rate-Hour [USD]
Dozer | 2000 | 2000 | 250 | 13
Excavator | 1100 | 1100 | 120 | 13
Cherry Pick | 325 | 325 | 95 | 10
Boat Rental | ­ | ­ | 85 | ­
Transformer Oil Plant | 900 | 900 | 80 | 45